Specifications for

INSUL-TEK® Fiber-Clad® Double Wall Containment Piping

General:

All double wall containment piping shall be Fiber-Clad® Containment Piping as manufactured by Insul-Tek ® Piping Systems, Inc.  All straight lengths of pipe, fittings and accessories shall be factory prefabricated by the manufacturer.  No field fabrication of fittings or accessories will be allowed.  All secondary containment welds completed at the factory shall be 100% air tested prior to shipment.  The containment piping system shall be drainable and air pressure testable.  Contractor fabricated systems, whether fabricated on-site or off-site shall not be allowed.  The containment piping manufacturer shall supply a complete design submittal including; engineered drawings, catalog cut sheets, and a full pipe stress analysis in accordance with ANSI B31.3 latest edition.  The calculations shall be stamped by a Registered Professional Engineer.

Carrier Pipe:

The Carrier pipe shall be carbon steel, beveled for welding.  Pipe sizes 2” through 10” shall be Schedule 40 A53 Grade B, E.R.W. steel.  Sizes larger than 10” shall be standard wall thickness.

Pipe sizes 1-1/2” and smaller shall be A106/A53 seamless type.  All joints for pipe 2-1/2” and larger in size shall be butt welded.  Sizes 2” and smaller shall be socket welded.

Secondary Containment Casing:

The secondary containment casing shall be carbon steel, in accordance with ASTM A-139 grade B, ASTM A-135 Grade B, or ASTM A-53 Grade B.  The containment casing shall be the thickness as listed below:

Conduit Size               Conduit Thickness

3” – 4”                      Sch. 10 or .120

5” – 26” 	         10 Gauge or .134

28” – 36”                  06 Gauge or .187

The carbon steel containment casing shall have a Fiberglass Reinforced Plastic (FRP) external cladding of not less than 100 mils thickness.  The F.R.P. Cladding shall be filament wound directly on to the carbon steel casing.  All field joints on the containment casing shall be welded, air-tested and covered with heat shrink sleeve or covered with a hand lay-up of fiberglass cloth and polyester resin.

Pipe Supports:

All pipe within the containment casing shall be supported at not more than 10’ intervals.  The supports shall be designed to allow for draining of the containment casing in the event of a leak.

Leak Detection/ Location Systems:

The leak detection/ location system shall utilize a continuous monitoring cable in conjunction with an alarm/ locator module.  The leak detection system shall be capable of not only detecting a leak, but also be able to pinpoint the exact location of the leak.  The leak detection cable shall be capable of detecting water, aqueous liquids (acid, bases and water), or hydrocarbons, depending on the type of fluid being conveyed.  The containment piping system shall be designed to allow pulling of a leak detection cable into the containment casing.  To facilitate pulling of the cable, pull supports shall be located a maximum of 500 feet apart for straight runs and reduced by 150 feet for every 90⁰ change in direction.

Installation:

The installing contractor shall weld the carrier pipe in accordance with ANSI B31.3 latest edition.  After welding, the carrier pipe shall be hydrostatically tested to 50 psig or 1-1/2 times the operation pressure, whichever is greater.  The containment casing shall be air tested to 10 psig after welding.  The test pressures shall be held

for no less than (1) one hour.  The containment casing shall be kept clean and dry at all periods during installation.  The installing contractor must adhere to all directions relating to the installation provided by the containment piping system manufacturing.

Backfill:

A 4” layer of sand or fine gravel shall be tamped in the trench to provide a stable and uniform bedding for the conduit system.  Once the conduit system is in place, the trenches shall be carefully backfilled and hand tamped in 6” layer until a cover of at least 24” from the top of the pipe has been achieved.  The first 12” of backfill shall be sand or fine gravel less than ½” diameter.  The remainder of the backfill shall be void rocks, frozen earth and foreign material over 6” in diameter.  The trench shall be compacted to comply with H-20 Highway loading.