Specifications for

INSUL-TEK® 250 Copper Piping

A preinsulated piping system for above and below ground use on systems with temperatures ranging from -350⁰ F to 250⁰ F.

MATERIALS:

All pipe shall be factory preinsulated INSUL-TEK® 250 Copper, as manufactured by Insul-Tek® Piping Systems, Inc.

Carrier Pipe:

Type K, L, or M Hard Drawn Copper Tubing to ASTM B-88 and WWT-799.

INSULATION:

Foamed in-place closed cell polyurethane foam completely filling the annulus between the carrier pipe and jacketing.

Typical Mechanical Properties

Core Density

2.1 P.C.F., ASTM D-1622

Closed Cell Content

90 to 95%                ASTM D-2856

“K” Factor, BTU/hr.in/ft²/⁰F @ 73⁰ F

.16                       ASTM C-518

OUTER CASINGS:

HDPE:

Black High Density Polyethylene

Resin Type III, Grade P34,

Under ASTM D-1248

Tensile Yield Strength

3300 psi ASTM D-638

Ultimate Elongation

850%    ASTM D-638

Tangent Flexural Modulus

175,000 psi ASTM D-790

FRP:

Fiberglass Reinforced Plastic (FRP) comprised of isophthalic polester resin and fiberglass strand.  Minimum wall thickness to be a minimum 100 mils.  Vinylester resin is also available.  Please consult factory for recommendation.

*For optional casings, consult the Casing Selection Guide.

FITTINGS:

All fittings shall be WROT pressure fittings complying with ANSI B16-22 and shall be factory prefabricated.  The outer casing shall be constructed of the same material as the outer casing on the straight lengths of pipe.

SOLDERING & BRAZING:

Silver solder or brazing alloys with a melting point at or aboe 1100⁰ F is recommended.

95/5 solder is recommended.

FIELD JOINTS:

After connecting the straight lengths of copper pipe and hydro-static testing, the field joints shall be insulated utilizing a pour foam, a PVC wrap around mold and a heatshrink wrap.

ANCHORS:

All pipe shall be anchored per manufacturers.

BACKFILLING:

The trenches shall be carefully backfilled and hand tamped in 6” layers until a cover of at least 24” from the top of the pipe has been achieved.  The first 6” of backfill shall be sand or fine gravel less than ½” in diameter.  The remainder of the backfill shall be free of rocks, frozen earth, and foreign material over 6” in diameter.  The trench shall be compacted to comply with H-20 highway loading.