Specifications for

INSUL-TEK® 250 Steel Piping

A preinsulated piping system for above and below ground use on systems with temperatures ranging from -350⁰ F to 250⁰ F.

MATERIALS:

All pipe shall be factory preinsulated INSUL-TEK® 250 Steel, as manufactured by Insul-Tek® Piping Systems, Inc.

Carrier Pipe:

Schedule 40 or Schedule 80 ASTM A53 Grade B beveled for welding, or other as specified.

INSULATION:

Foamed in-place closed cell polyurethane foam completely filling the annulus between the carrier pipe and jacketing.

Typical Mechanical Properties

Core Density

2.1 P.C.F., ASTM D-1622

Closed Cell Content

90 to 95%                ASTM D-2856

“K” Factor, BTU/hr.in/ft²/⁰F @ 73⁰ F

.16                       ASTM C-518

OUTER CASINGS:

HDPE:

Black High Density Polyethylene

Resin Type III, Grade P34,

Under ASTM D-1248

Tensile Yield Strength

3300 psi ASTM D-638

Ultimate Elongation

850%    ASTM D-638

Tangent Flexural Modulus

175,000 psi ASTM D-790

FRP:

Fiberglass Reinforced Plastic (FRP) comprised of isophthalic polester resin and fiberglass strand.  Minimum wall thickness to be a minimum 100 mils.  Vunylester resin is also available.  Please consult factory for recommendation.

*For optional casings, consult the Casing Selection Guide.

FITTINGS:

All fittings will conform to the pipe type and size and will be factory prefabricated.  The outer casing on the fittings shall consist of the same material as utilized on the straight lengths of pipe.

FIELD JOINTS:

After welding and hydrostatic testing, all field joints shall be insulated and sealed following manufacturer’s recommendations.

ANCHORS:

Prefabricated steel anchor plates shall be welded to the internal piping.  A steel ring with the same diameter as the casing shall be tightly sealed to the ring with a heat shrinkable sleeve or a hand lay-up of FRP by the manufacturer.  On pipe sizes up to 10” in size, 3/8” thick steel plate shall be used, ½” thick steel plate for pipe sizes 12”- 16”, and ¾” thick steel plate for all larger pipe sizes.

BACKFILLING:

The trenches shall be carefully backfilled and hand tamped in 6” layers until a cover of at least 24” from the top of the pipe has been achieved.  The first 6” of backfill shall be sand or fine gravel less than ½” in diameter.  The remainder of the backfill shall be void of rocks, frozen earth, and foreign material over 6” in diameter.  The trench shall be compacted to comply with H-20 highway loading.